SOP-04 — Substation / Equipment Failure

A substation breaker, transformer, or protection device has failed or tripped and will not reset.

| SOP # | SOP-04 | Applies to | System operators, substation technicians, protection engineers |
| --- | --- | --- | --- |
| Owner | Outage Operations | Review | Annual |

1. When this SOP applies

- Substation breaker locked out or a relay that will not reset.

- Transformer alarm (temperature, gas, differential) or SCADA-reported equipment failure.

2. Immediate actions

- Do NOT repeatedly re-energize into a fault — one controlled attempt only if procedures allow.

- Review SCADA and relay targets to identify the faulted equipment.

- Dispatch a substation technician and engage a protection engineer.

- Switch load to an alternate feeder/source where one is available.

3. Roles

- System Operator: Reads SCADA/relay targets; directs switching.

- Substation Technician: Inspects equipment on site under lockout/tagout.

- Protection Engineer: Interprets relay operation and authorizes re-energization.

4. Procedure

- Isolate the failed equipment and apply lockout/tagout.

- Transfer load to an alternate source to restore customers where possible.

- Assess the equipment (e.g., transformer gas/temperature, breaker condition).

- Arrange repair or replacement; order a spare if needed.

- Return to service per switching order once cleared by the protection engineer.

5. Safety

- Full arc-flash PPE inside the substation.

- Strict lockout/tagout before any contact with equipment.

6. Communications

- Notify affected regional ops of the load transfer and any remaining customers out.

- Keep the duty supervisor informed of repair timeline.

7. Restoration & closeout

- Confirm equipment returned to service and protection in-service.

- Record failure cause and any spare/inventory impact.

8. Escalation thresholds

- Loss of a transmission-level substation: notify the regional grid/transmission operator at once.

- If no alternate feeder exists and many customers are out, also invoke SOP-02.